## Data Delivery Points
Expected Data Delivery Points
The following illustrates a generic view of participant recruitment with an illustration of which datasets and reports are expected at each point.
Further detail is as follows for each dataset
| Consumer Journey Stage | Comment
| (1) Participant Info | Only required for homes /participants selected for survey
| (2) Recruitment | Only required for homes /participants selected for survey
| (3) Home Suitability Survey | For all homes surveyed, irrespective of whether they progress to design. Where a home survey is not completed for any reason, a partially completed dataset shall be provided. Dataset (4.1) may also be provided (partially completed) to record the reason for non-progression of the property.
| (4.1) System Design Information | For all homes for which design calculations are performed, irrespective of whether home progresses to installation. For homes that do not progress past the Home Suitability stage, a partially completed (4.1) which contains the reason(s) for non-progression may be provided at the same time as dataset (3).
| (4.2) Installation Database | For all heat pump installations undertaken as part of this project.
| (5.0) Monitoring (not included in this dataset) | For all heat pump installations undertaken as part of this project.
Further project reports and information up to the installation stage of the project:
| Report | Detail
| Data Documentation Report: Recruitment, Survey, Design, and Installation Data | A report which provides an overview of the Receuitment, Survey, Design and Installation Dataset including the collation and quality assurance processes undertaken to create the dataset.
| Installation Statistics Report | A report outlining the project installation targets and statistics.
| Participant Recruitment Report | A report providing the findings on the participant recruitment stage of the project including recruitment approaches and reasons participants joined the project.
| Home Suitability Surveys and Installation Report | A report providing interim findings on the home survey, design and installation stages of the project.
| Interim Insights From Heat Pump Performance Data | A report highlighting the insights and findings from the analysis of the heat pump performance data at an interim stage in the performance monitoring.
| Interim Heat Pump Performance Data Analysis Report | A report detailing the data quality checking and cleansing processes and highlighting the insights and findings from the analysis of the heat pump performance data at an interim stage in the performance monitoring.
Mass Recruitment Effort
Delivery Contractor
"Triage"
Home Suitability Surveys
Technical Surveys & System Design
Monitoring & Support
(2) Recruitment
(1) Participant Info (GDPR)
(3) Home Suitability Survey
(4.1) System Design Information
(4.2) Installation Database
(5.0) Monitoring
Triage summary report
System Installation

## Data Dictionary Prop, Des & Ins
The Property, Design and Installation dataset is available from USmart.
https://usmart.io/org/esc/discovery?order=statistic.viewCount&tags=BEIS%20EoH%20Project&limit=20&offset=0
Consumer Journey Stage | Data Item | Field name | Type | Description | Units | Acceptable Values | Attributes / Notes
- | Responsible Delivery Contractor | Delivery_Contractor | String | The name of the Delivery Contractor who recruited this participant | None | E.ON OVO Warmworks
- | Property ID Number | Property_ID | String | A randomly allocated pseudonymised identifier for each home. | None | EOH<number> | One per home. Randomly allocated replacing the original House_ID which was the Delivery Contractors customer reference number. Will be replicated in monitoring datasets.
1 | Postcode - first part | Postcode_1 | String | The first half of the property postcode | None
1 | Age of the lead participant | Participant_Age | Integer | The age of the lead participant at the time of recruitment into the project | Years | <number> | This was derived from the date of birth provided during recruitment. This was optional data which some participants chose not to provide.
1 | Employment status | EmployStatus | String | The employment status of the lead participant | None | Working Full time (>30hrs) Working Part time Unfit for work Carer Unemployed Training or Education Stay at home parent Retired Prefer not to say NOT AVAILABLE
1 | Type of employment | EmployType | String | The type of employment of the of the lead participant / householder | None | Manager Professional Supervisor Clerical Skilled Manual Worker Semi and unskilled manual worker Casual worker Pensioner Retired Unemployed/Benefits Prefer not to say NOT AVAILABLE
1 | Household gross annual Income | HouseIncome | String | Total household gross income from all sources. | GBP | Prefer not to say £0 - 12,500 £12,501 - 16,200 £16,201 - 20,000 £20,001 - 25,000 £25,001 - 30,000 £30,001 - 40,000 £40,001 - 50,000 £50,001+
2 | Date of initial contact | Date_Contact | Date | The date on which contact was made with the participant following their initial registration | Date | <date> after 01-06-2020 | Date provided in ISO format yyyy-mm-dd. When downloaded from Usmart it includes a timestamp so will be formated yyyy-mm-ddT00:00:00.000Z
2 | Tenure of property | Tenure | String | The tenure type the participant has for the property | None | Owner-Occupied Rented (Private) Rented (Social)
2 | Length of time resident in property (years) | Tenure_Length | Real Number | The length of time that the participant been resident in the property | Years | <number>
2 | Social Group (as per Socioeconomic Status) | Social_Group | String | The social group to which the participant belongs as assessed by the DC | None | AB C1 C2 DE | AB. Higher and intermediate managerial, administrative or professional occupation C1. Supervisory, clerical and junior managerial, administrative or professional C2. Skilled manual workers DE. Semi and unskilled manual workers, state pensioners, casual or lowest grade workers, unemployed with state benefits only
2 | Awareness of Heat Pumps | HP_Awareness | Integer | A score to indicated what level of awareness a household has of heat pump systems at the start of this project | None | 1 2 3 4 5 | 1 = No prior awareness of heat pumps at all 2 = Had heard of heat pumps but no real understanding of what they are or how they work 3 = Aware of heat pumps as a potential heating system, may have some awareness of how they work 4 = Reasonable understanding of heat pumps and how they work and the implications of having one as a home heating system 5 = Extremely knowledgeable and understands heat pump systems well and how they work. good understanding of their operation and implications for a home. May have prior experience of living with and operating such systems
2 | Reason for interest in the project | Reason_Sustainability | Boolean | Participant is interested or keen to take action to reduce their environmental impact and/or to move to a greener/renewable heating system | None | Yes No
2 | Further explanation of above reason | Sustainability_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
2 | Reason for interest in the project | Reason_Future | Boolean | Participant is keen to "future proof" their house / heating system investment by adopting a low carbon technology | None | Yes No
2 | Further explanation of above reason | Future_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
2 | Reason for interest in the project | Reason_Upgrade | Boolean | Participant is looking for a way to upgrade their heating system and views a Heat pump as a way of doing this. | None | Yes No
2 | Further explanation of above reason | Upgrade_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
2 | Reason for interest in the project | Reason_Building | Boolean | Participant is undertaking building / refurbishment works to their property and would like to take advantage of this | None | Yes No
2 | Further explanation of above reason | Building_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
2 | Reason for interest in the project | Reason_Financial | Boolean | Participant is attracted to the fact that the system will be provided free of charge. | None | Yes No
2 | Further explanation of above reason | Financial_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
2 | Reason for interest in the project | Reason_Technology | Boolean | Participant is intrigued by the technology and/or keen to adopt new technology into their home. | None | Yes No
2 | Further explanation of above reason | Technology_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
2 | Reason for interest in the project | Reason_Research | Boolean | Partisan is keen to support / take part in this research project | None | Yes No
2 | Further explanation of above reason | Research_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
2 | Reason for interest in the project | Reason_Planned | Boolean | Participant is already planning to change to a heat pump so this is an opportunity to do so. | None | Yes No
2 | Further explanation of above reason | Planned_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
2 | Reason for interest in the project | Reason_Replacement | Boolean | Existing heating system is in need of replacement anyway so this is an opportunity to achieve that aim | None | Yes No
2 | Further explanation of above reason | Replacement_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
2 | Reason for interest in the project | Reason_Other | Boolean | Any other reason | None | Yes No
2 | Further explanation of above reason | Other_exp | Text | Any further explanation given by the participant that helps expand on the reason code given above | None | <free text> | Free text This is not mandatory data so blanks may exist for this reason.
3 | Date of survey | Date_survey | Date | The date that the survey of the home was undertaken. If there was more than one visit, this is the date of the first. | Date | <date> after 01-06-2020 | Date provided in ISO format yyyy-mm-dd. When downloaded from Usmart it includes a timestamp so will be formated yyyy-mm-ddT00:00:00.000Z. For some properties, a date for a survey exists however little or no survey data is available. This is either because the survey didn’t take place or was abandoned early, usually due to participants being unavailable or deciding not to continue with the programme.
3 | Name of surveyor organisation | Name_Survey | String | The name of the organisation that carried out the home survey | None | <free text> | Note that inclusion of surveyors in this dataset and this project does not act as an endorsement of those surveyors by BEIS or the other project partners, it simply indicates that these companies undertook the surveys on this project. Also note that the (un)availability of some or all survey data should not be an indication of surveyors performance on the project, survey data may have been collected in full or part for many different reasons out of the surveyors control. Some of the surveyors are individuals trading under their name. In these instances, the data has been retracted and replaced with "Restricted Data" due to GDPR regulations.
3 | Property Type | House_Type | String | Describes the type of property as House, Flat or Maisonette. This is the type differentiator for dwellings | None | House Maisonette Flat | A bungalow would be recorded here is a "House" but identified through the number of storeys
3 | Property built form | House_Form | String | Describes the building type of the Property as Detached, Semi-Detached, End/Mid-Terrace or Flat. Together with the Property Type, the Build Form produces a structured description of the property | None | Mid-Terrace End- Terrace Detached Semi-Detached Flat
3 | House environment | House_Env | String | Summary description of where the house is located | None | Urban Suburban Rural | These classifications are as used on current EPCs. Where an EPC doesn't exist, they were recorded at the surveyors discretion.
3 | Age of Property | House_Age | String | Which age band does the property fall into. | Year | <date bands> pre/before YYYY YYYY - YYYY YYYY+ / YYYY onwards | E.On recorded these as standard EPC date bands for England & Wales. OVO and Warmworks recorded as the project date bands as per the ITT requirements.
3 | Current SAP energy efficiency score (if known) | House_SAP | String | The EPC band of the property based on the most recent EPC assessment prior to the survey (if available / known) | None | A letter from A - G
3 | No. Adults | No_Adults | Integer | The number of people aged 18 years or above that live in the property | None | <number> | Note that the number of adults and children should be added together to gain the total number of occupants.
3 | No. Children | No_Child | Integer | The number of people aged 17 years or below that live in the property | None | <number> | Note that the number of adults and children should be added together to gain the total number of occupants.
3 | No. storeys | No_Storeys | Integer | Number of habitable storeys in the property | None | <number> | A loft conversion counts as a habitable storey - so a nominally 2-storey house with a loft conversion should be recorded as 3-storey as an example.
3 | Total household floor space (m2) | Total_Floor_Area | Real Number | The total useful floor area is the total of all enclosed spaces measured to the internal face of the external walls, i.e. the gross floor area as measured in accordance with the guidance issued from time to time by the Royal Institute of Chartered Surveyors or by a body replacing that institution. | m2 | <number> less than 500
3 | Number of habitable rooms | Habitable_Rooms | Integer | The number of habitable rooms in the property. | None | <number> | Habitable rooms include any living room, sitting room, dining room, bedroom, study and similar; and also a non-separated conservatory. A kitchen/diner having a discrete seating area (with space for a table and four chairs) also counts as a habitable room. A non-separated conservatory adds to the habitable room count if it has an internal quality door between it and the dwelling. Excluded from the room count are any room used solely as a kitchen, utility room, bathroom, cloakroom, en-suite accommodation and similar and any hallway, stairs or landing; and also any room not having a window. Based on this definition, it is therefore possible to have a larger number of heated rooms than habitable rooms.
3 | Number of bedrooms | Bedrooms | Integer | The number of bedrooms in the property | None | <number>
3 | Number of heated rooms | Heated_rooms | Integer | The number of heated rooms in the property. | None | <number> | This may be greater than the number of habitable rooms in the property.
3 | Average height of the storeys in the property (m) | Floor_Height | Real Number | The average height of the storeys in the property | metres | <number> between 1.8m and 5.0m
3 | Wall construction | Wall_Type | String | Description of the predominant construction of the external walls of the property | None | Solid_No_insulation Solid_Insulated Cavity_Insulated Cavity_No_insulation Cavity_Unknown
3 | Floor Type | Floor_Type | String | Type of flooring in rooms on the ground floor of the property (excluding corridors, hallways etc). | None | Solid Suspended Mix
3 | Roof type | Roof_Type | String | Predominant roof type in terms of design/construction | None | Flat Pitched Another Dwelling Above | "Another Dwelling Above" can apply to flats only
3 | Predominant Glazing Type | Glazed_Type | String | The type of glazing. From British Fenestration Rating Council or manufacturer declaration. | None | Single Double Triple
3 | Mains gas flag | Mains_Gas_Flag | Boolean | Whether mains gas is available. Yes means that it is connected to the gas grid with a gas meter | None | Yes No | A property with a disconnected gas pipe would be recorded as "No"
3 | Current Heating System main - Fuel | Main_Fuel | String | The fuel used by the primary heating system within the property at the point of survey | None | Oil LPG Gas Electricity Wood Coal | Gas refers to mains natural gas whereas LPG refers to any canned or liquified gas.
3 | Current Heating System - Primary Heat Source | Heat_Primary_Source | String | A description of the heat source of the primary heating system at the point of survey | None | Gas Boiler - Combi Gas Boiler - Standard Gas - Warm air LPG Boiler LPG Boiler - Combi Oil Boiler Oil Boiler - Standard Oil - Combi Electric - Storage Electric - Direct Electric - Warm air Electric Boiler Biomass Boiler Fire - Wood Fire - Coal Fire - Gas Fire - LPG Fire - Electric None
3 | Current Heating System - secondary Heat Source | Heat_Secondary_Source | String | A description of the heat source of any secondary heating system at the point of survey | None | Gas Boiler - Combi Gas Boiler - Standard Gas - Warm air LPG Boiler LPG Boiler - Combi Oil Boiler Oil Boiler - Standard Oil - Combi Electric - Storage Electric - Direct Electric - Warm air Electric Boiler Biomass Boiler Fire - Wood Fire - Coal Fire - Gas Fire - LPG Fire - Electric Unknown None
3 | Any existing thermal store? | TS_Existing | String | The type of thermal storage used to support provision of Domestic Hot Water, if any | None | Water PCM None | PCM = Phase Change Material
3 | Size of existing thermal store | TS_Existing_Size | Integer or String | The size/capacity of any existing thermal store use to support provision of DHW. | Litres, kWh or None (see notes) | <number> Normal Medium Large Unknown | The number is the size of the store in either litres for water stores or kWh for PCM stores. If the exact size is not known or cannot be ascertained, the size may be recorded as normal, medium or large (with normal being the smaller of the 3 sizes). If unknown, it can be assumed that no access to the thermal store was available or granted. Some surveyors have indicated directly that no access was available, others included the size of the store as 0 if not known, where 0 values existed these have been replaced with null.
3 | Number of rooms with underfloor heating | No_Underfloor | Integer | Number of rooms with underfloor heating supplied from the primary home heating system | None | 0 <number> | This only includes underfloor heating provided by the primary heat source. If a house is primarily gas central heating for example, but has a single room (e.g. bathroom) with an electric underfloor heating system, this would not be included.
3 | Other gas appliances - fires | Existing_Fires | Integer | Number of connected gas heating appliances in the property (in addition to any gas boilers) | None | 0 <number>
3 | Other gas appliances - cookers | Existing_Cooking | Integer | Number of connected gas cooking appliances in the property | None | 0 <number>
3 | Does the property have an outside space potentially suitable for a GSHP? | Outside_Space | String | Does the survey suggest that the home has space that could be used for a GSHP installation, and if so which type of GSHP array. | None | Yes - Ground Loop Yes - borehole Yes No | This is an indication only based on the experience of the surveyor - at the point of survey a detailed design calculation of the required area will not have been completed. Note that some of the surveyors indicated which type of GSHP may be possible however others only indicated that a GSHP may be possible.
3 | Does the property have suitable access points to allow a GSHP installation to occur? | Outside_Access | Boolean | An assessment as to whether any suitable outside space for a GSHP is likely to be accessible by the necessary equipment for excavations, etc | None | Yes No | This is an indication only based on the experience of the surveyor - it is recognised at this time that a detailed design calc of required area will not have been completed
3 | Current annual energy consumption - electricity | Elec_currentuse | Real Number | Annual electricity consumption of the household based on the previous X years of bills | kWh | <number> between 100 and 25,000 | Some values were listed as "Unknown", these have been changed to "null".
3 | Current annual energy consumption - gas | Gas_currentuse | Real Number | Annual Gas consumption of the household based on the previous X years of bills | kWh | <number> between 100 and 50,000 | Some values were listed as "Unknown", these have been changed to "null".
4.1 | Peak space heating load from MCS design calculations | MCS_SHLoad | Real Number | Peak space heating load calculated using the MCS design calculations. | kW | <number>
4.1 | Peak building heat Loss from MCS Design Calculations | MCS_Hloss | Real Number | The properties peak heat loss per m2 calculated using the MCS Design Calculations. | W/m2 | <number>
4.1 | Annual space heating demand from MCS Design Calculations | MCS_SHAnnual | Real Number | Estimated annual heat pump energy output for space heating calculated using the MCS Design Calculations. | kWh/yr | <number> between 100 and 50,000 | To attain the estimated total heat pump energy output, sum the MCS_SHAnnual and MCS_DHWAnnual.
4.1 | Annual hot water energy demand from MCS Design Calculations | MCS_DHWAnnual | Real Number | Estimated annual heat pump energy output for domestic hot water calculated using the MCS Design Calculations. | kWh/yr | <number> | To attain the estimated total heat pump energy output, sum the MCS_SHAnnual and MCS_DHWAnnual.
4.1 | Annual immersion heater energy requirement from MCS Design Calculations | MCS_Immersion | Real Number | Estimated annual immersion heater energy output calculated using the MCS Design Calculations. | kWh/yr | <number>
4.1 | Interim Assessment: Heat Pump suitability - ASHP | Suit_ASHP | String | Interim Assessment: Is an Air Source Heat Pump suitable for the home, or could it be suitable with additional home upgrade measures? | None | Yes Yes with additional measures No | This is a subjective assessment based on the skills and experience of the assessor, and in the context of the systems and budgets available within the project. It is only an interim assessment at the beginning of the design process and is not based on a full assessment and detailed design for the heat pump type and all possible products. As a result of these factors, the suitability decision may be overturned later in the design phase of the customers journey. However, the decision made at this interim stage within the survey and design process is often taken as face-value and can channel the decision not to proceed to the next step. As a result of these factors, the assessment result should not be used as an objective measure of heat pump suitability. Yes = home is suitable now, no additional energy efficiency measures are required. Yes with additional measures = home would be suitable after the addition of defined energy efficiency measures available within the project / budget. (Project and budget constraints are defined within the "Home Surveys and Install Report" and the "Data Documentation Report") No = home will not be suitable, even after addition of energy efficiency measures available within the project / budget. Note that properties were rejected if the estimated cost of the energy efficiency measures required exceeded the project budget.
4.1 | Interim Assessment: Heat Pump suitability - GSHP | Suit_GSHP | String | Interim Assessment: Is a Ground Source Heat Pump suitable for the home, or could it be suitable with additional home upgrade measures? | None | Yes Yes with additional measures No | This is a subjective assessment based on the skills and experience of the assessor, and in the context of the systems and budgets available within the project. It is only an interim assessment at the beginning of the design process and is not based on a full assessment and detailed design for the heat pump type and all possible products. As a result of these factors, the suitability decision may be overturned later in the design phase of the customers journey. However, the decision made at this interim stage within the survey and design process is often taken as face-value and can channel the decision not to proceed to the next step. As a result of these factors, the assessment result should not be used as an objective measure of heat pump suitability. Yes = home is suitable now, no additional energy efficiency measures are required. Yes with additional measures = home would be suitable after the addition of defined energy efficiency measures available within the project / budget. (Project and budget constraints are defined within the "Home Surveys and Install Report" and the "Data Documentation Report") No = home will not be suitable, even after addition of energy efficiency measures available within the project / budget. Note that properties were rejected if the estimated cost of the energy efficiency measures required exceeded the project budget.
4.1 | Interim Assessment: Heat Pump suitability - HT ASHP | Suit_HTASHP | String | Interim Assessment: Is a High Temperature Air Source Heat Pump suitable for the home, or could it be suitable with additional home upgrade measures? | None | Yes Yes with additional measures No | This is a subjective assessment based on the skills and experience of the assessor, and in the context of the systems and budgets available within the project. It is only an interim assessment at the beginning of the design process and is not based on a full assessment and detailed design for the heat pump type and all possible products. As a result of these factors, the suitability decision may be overturned later in the design phase of the customers journey. However, the decision made at this interim stage within the survey and design process is often taken as face-value and can channel the decision not to proceed to the next step. As a result of these factors, the assessment result should not be used as an objective measure of heat pump suitability. Yes = home is suitable now, no additional energy efficiency measures are required. Yes with additional measures = home would be suitable after the addition of defined energy efficiency measures available within the project / budget. (Project and budget constraints are defined within the "Home Surveys and Install Report" and the "Data Documentation Report") No = home will not be suitable, even after addition of energy efficiency measures available within the project / budget. Note that properties were rejected if the estimated cost of the energy efficiency measures required exceeded the project budget. In some cases, the HT_ASHP has been deemed unsuitable for a property whereas an ASHP has been deemed suitable. For these cases, the suitability is likely down to customer or installer preference, or the HT_ASHP has been discounted as a result of the lower temperature variation being an option.
4.1 | Interim Assessment: Heat Pump suitability - Hybrid | Suit_Hybrid | String | Interim Assessment: Is a Hybrid Heat Pump suitable for the home, or could it be suitable with additional home upgrade measures? | None | Yes Yes with additional measures No | This is a subjective assessment based on the skills and experience of the assessor, and in the context of the systems and budgets available within the project. It is only an interim assessment at the beginning of the design process and is not based on a full assessment and detailed design for the heat pump type and all possible products. As a result of these factors, the suitability decision may be overturned later in the design phase of the customers journey. However, the decision made at this interim stage within the survey and design process is often taken as face-value and can channel the decision not to proceed to the next step. As a result of these factors, the assessment result should not be used as an objective measure of heat pump suitability. Yes = home is suitable now, no additional energy efficiency measures are required. Yes with additional measures = home would be suitable after the addition of defined energy efficiency measures available within the project / budget. (Project and budget constraints are defined within the "Home Surveys and Install Report" and the "Data Documentation Report") No = home will not be suitable, even after addition of energy efficiency measures available within the project / budget. Note that properties were rejected if the estimated cost of the energy efficiency measures required exceeded the project budget.
4.1 | Recommended Heat Pump system type | HP_Recommend | String | Which type of heat pump system is recommended for this property? | None | ASHP GSHP HT_ASHP Hybrid None - Installation not recommended | This is the system designers recommendation following design work and accounting for input from the participant with respect to preferences. Note that decisions may be influenced by project limitations and targets. ASHP = Air Source Heat Pump GSHP = Ground Source Heat Pump (either borehole or ground loop) HT_ASHP = High-Temperature Air Source Heat Pump Hybrid = Hybrid Heat Pump System (either monobloc unit containing HP and boiler or separate HP and gas boiler)
4.1 | Reason for not progressing with install | HP_NoRec_R1 | String | If the designer does not recommend progressing to installation, what is the main reason? | None | See Reason Codes on "Reason Codes Tab" | Note that decisions may be influenced by project limitations and targets.
4.1 | Reasons for not progressing with install | HP_NoRec_R2 | String | If the designer does not recommend progressing to installation, what is the secondary reason (if any)? | None | See Reason Codes on "Reason Codes Tab" | Note that decisions may be influenced by project limitations and targets.
4.1 | Additional measures recommended to permit HP system installation | Measures_Recommend | String | List of additional measures suggested to be done in addition to the installation of the suggested system | None | None required Loft Insulation Wall insulation Window replacement Door replacement Draft Proofing Heat Emitters Sound Barrier | This field may list more than one measure. Note that in some cases, the designer has elaborated on the type of wall insulation (e.g. Cavity Insulation) also, where only "Barrier" is listed, this refers to the installation of a Sound Barrier. In addition, only some designers have noted where planning permission may be required and others have noted where a thermal store may be required.
4.1 | Estimated system cost - Heating system components (£) | EstCost_System | Real Number | Estimated cost of heating system components deemed to be required - Heat pump, thermal store, control system, heat emitters, pipes, etc | GBP | <number> between £4,000 to £60,000 | These costs were estimated at the time of design so estimated system costs may have changed since installation. In addition, these costs were estimated based on the project parameters and contracts (which includes multiple installations) so may vary when compared with a single installation. Note that the estimated system cost and ancillary cost can be summed together to attain a total cost estimate.
4.1 | Estimated system cost - ancillary measures (£) | EstCost_Ancillary | Real Number | Estimated cost of any additional home upgrade measures deemed to be required, e.g. insulation, windows, etc | GBP | <number> | These costs were estimated at the time of design so estimated system costs may have changed since installation. In addition, these costs were estimated based on the project parameters and contracts (which includes multiple installations) so may vary when compared with a single installation. Note that the estimated system cost and ancillary cost can be summed together to attain a total cost estimate.
4.1 | Estimated system cost - annual running (£) | EstCost_Running | Real Number | Estimated annual cost of running the proposed heating and hot water system. | GBP/yr | <number> | These costs were estimated at the time of design based on the Estimated Electricity and Gas tariffs. These will have changed based on energy price changes since design.
4.1 | Estimated system cost - electricity tariff assumption (p/kWh) | EstCost_Etariff | Real Number | The electricity tariff assumed for calculating the running costs as presented to the homeowner. | p/kWh | <number> between 10 and 25 | Estimated at the time of design.
4.1 | Estimated system cost - gas tariff assumption (p/kWh) | EstCost_Gtariff | Real Number | The gas tariff assumed for calculating the running costs as presented to the homeowner. | p/kWh | <number> between 2 and 10 | Estimated at the time of design.
4.1 | Does the participant wish to progress to install? | Part_Install_Decision | Boolean | The participant decision as to whether to progress to an installation. | None | Yes No | This decision can occur at any time in the process
4.1 | Main reason for participant not progressing to install | Part_No_Reason1 | String | The participant's primary reason for not wishing to progress within the project. | None | See Reason Codes on "Reason Codes Tab" | Only answered if installation is not to progress due to a participant decision
4.1 | Secondary reason for participant not progressing to install | Part_No_Reason2 | String | The participant's secondary reason (if any) for not wishing to progress within the project. | None | See Reason Codes on "Reason Codes Tab" | Only answer if installation is not to progress due to participant rejection A second reason is optional
4.2 | Start date of installation | Date_Installation | Date | The date on which the installation of the heat pump system commenced | Date | <date> after 01-06-2020 | Date provided in ISO format yyyy-mm-dd. When downloaded from Usmart it includes a timestamp so will be formated yyyy-mm-ddT00:00:00.000Z
4.2 | Name of installation organisation | Name_Install | String | The name of the organisation that carried out the installation | Name | <free text> | All installers on this project were MCS accredited installers at the time of the installation. A full list of MCS accredited heat pump installers can be found on the MCS website. Note that inclusion of installers in this dataset and this project does not act as an endorsement of those installers by BEIS or the other project partners, it simply indicates that these companies who performed the installations on this project. Also note that the performance of the heat pump which has been installed is not a definite reflection of the installers competence or install quality. Many factors such as, home type, heating set points, weather, system type, heat pump model and install quality can affect the performance of the heat pump.
4.2 | Type of heat pump system installed | HP_Installed | String | The type of heat pump system that was installed | None | ASHP GSHP HT_ASHP Hybrid None - Installation not recommended | ASHP = Air Source Heat Pump GSHP = Ground Source Heat Pump (all installations are utilise boreholes. The OVO and E.On installations in flats are a shared borehole ground loop for a whole block of flats). HT_ASHP = High-Temperature Air Source Heat Pump Hybrid = Hybrid Heat Pump System (either monobloc unit containing HP and boiler or a separate split HP and gas boiler, the split hybrid system may make use of the existing boiler or include a new boiler installation)
4.2 | Heat Pump manufacturer | HP_Brand | String | The brand / manufacturer of heat pump that was installed | None | <free text> | Note that installation of specific brands and models of heat pump on project does not act as an endorsement of those brands and models by BEIS or the other project partners, it simply indicates that these models were deemed the most suited to the project requirements by the installers at the time of installation. A full list of MCS accredited heat pump models can be found on the MCS website. In addition, the performance of the heat pump may not be due exclusively to heat pump manufacturer or model, many factors including home type, heating set points, weather, system type, heat pump model and install quality can affect the performance of the heat pump.
4.2 | Heat Pump model | HP_Model | String | The model of heat pump that was installed | None | <free text> Where applicable - MCS product identification number. | Note that installation of specific brands and models of heat pump on project does not act as an endorsement of those brands and models by BEIS or the other project partners, it simply indicates that these models were deemed the most suited to the project requirements by the installers at the time of installation. A full list of MCS accredited heat pump models can be found on the MCS website. In addition, the performance of the heat pump may not be due exclusively to heat pump manufacturer or model, many factors including home type, heating set points, weather, system type, heat pump model and install quality can affect the performance of the heat pump.
4.2 | Size of installed Heat pump (in kW) | HP_Size_kW | Real Number | The rated size/capacity of the heat pump installed | kW | <number>
4.2 | Refrigerant which the installed heat pump uses | HP_Refrigerant | String | The refrigerant gas which is used within each heat pump | None | <free text> Refrigerant number beginning with "R"
4.2 | Space used for installation of ground loop or borehole (GSHP only) | GSHP_Space | Integer | The total area of external space, in m2, required for the installation of the Ground Loop and associated pipework | m2 | <number> | Where no ground source heat pump was installed, Warmworks have included a value of 0 in this column. Where a ground source heat pump is installed, only values of greater than 1 have been accepted. For the GSHP installations in flats, a Shared Ground Loop system has been utilised, therefore the space used is significant but can be divided by the number of flats (12 for OVO and 16 for E.On's installation).
4.2 | Type of thermal store used within the system | TS_Type | String | The type of thermal store used within the installed heat pump system | None | Water_New Water_Existing PCM_New PCM_Existing
4.2 | Size of thermal store - water (litres) | TS_Water_Size | Integer | Capacity of any water tank used as part of the system | litres | <number> | If multiple stores are fitted, this value is the total capacity of the system
4.2 | Size of thermal store - PCM (kWh) | TS_PCM_Size | Real Number | Capacity (in kWh) of any PCM thermal store used as part of the system. | kWh | <number> | If multiple stores are fitted, this value is the total capacity of the system
4.2 | Controls installed - No. zones controlled | HP_Control_Zones | Integer | Number of thermostat control zones linked to the heat pump control | None | <number> greater than 0
4.2 | No. low temp Heat emitters installed | Measures_emitters_LT | Integer | Number of additional/replacement Low Temperature heat emitters installed as part of the project | None | 0 <number> | 0 in Measures_emitters_LT, Measures_emitters_HT and Measures_Fanassist implies that no heat emitter changes were necessary as part of the installation.
4.2 | No. std Heat emitters installed | Measures_emitters_Std | Integer | Number of additional/replacement standard heat emitters installed as part of the project | None | 0 <number>
4.2 | No. fan assisted heat emitters installed | Measures_Fanassist | Integer | Number of fan assisted heat emitters installed as part of the project. | None | 0 <number>
4.2 | Any aesthetic technology installed alongside the heat pump. | HP_Aesthetic | String | An indicator of additional measures installed over and above the basic heat pump design - e.g. aesthetic enclosures. | None | None Enclosure
4.2 | Any Noise mitigating or blocking technology installed | HP_Noise | String | An indicator of additional measures installed over and above the basic heat pump design - e.g. enclosures / sound proofing | None | None Low Noise Heat Pump Enclosure Barrier | For the Warmworks installations, some of the heat pumps with quieter operation are listed as Low Noise Heat Pump, this is not replicated by the other Delivery Contractors. Specific noise data for each heat pump type may be obtained from the manufacturers websites.
4.2 | System cooling capable | Cooling | Boolean | Was the installed system configured to provide domestic cooling | None | Yes No
4.2 | Number of cooled rooms | Cooling_Rooms | Integer | The number of rooms to which cooling is provided | None | <number>
4.2 | Other gas systems replaced - fires | Fires_replaced | Integer | Number of mains gas or LPG fires replaced as part of the installation | None | <number>
4.2 | Other gas systems replaced - ovens/hobs | Cook_Replaced | Integer | Number of mains gas or LPG cooking appliances replaced as part of the installation | None | <number>
4.2 | Disconnection from gas grid | Gas_disconnect | Boolean | Was the property disconnected from the gas grid as part of the project? | None | Yes No | This records whether disconnection occurred, not if it is possible. Where inconsistencies between this and other data exists, data may have been replaced with "null".
4.2 | Additional measures installed to improve home thermal efficiency - Loft Insulation | Measures_Loft | Boolean | Was additional loft insulation installed as part of the project? | None | Yes No
4.2 | Additional measures installed to improve home thermal efficiency - Windows | Measures_Windows | Integer | Count of the number of windows upgraded as part of the project. | None | 0 <number>
4.2 | Additional measures installed to improve home thermal efficiency - External Doors | Measures_Doors | Integer | Count of the number of external doors upgraded as part of the project. | None | 0 <number> | A pair of doors (e.g. Patio doors) would recorded as two doors.
4.2 | Additional measures installed to improve home thermal efficiency - Wall Insulation | Measures_WI | String | What type of wall insulation was installed as part of the project, if any? | None | None Cavity EWI IWI Multiple | Cavity = Filling wall cavity with insulating material EWI = External Wall Insulation (usually for solid walls) IWI = Internal Wall Insulation (usually for solid walls) Multiple = Multiple Insulation Types (mix of wall types)
4.2 | Additional measures installed to improve home thermal efficiency - Draft proofing | Measures_DP | Boolean | Was draft proofing installed as part of this project? | None | Yes No
4.2 | Equipment Costs - Heat Pump (£) | Cost_HP | Real Number | Cost of the heat pump unit(s), including any general system pipework, pumps, etc | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future. All of the three Delivery Contractors recorded costs differently: OVO = Separated out heat pump costs and installation costs Warmworks = Accounted for all variations within heat pump costs (Cost_HP) and included a flat rate for installation costs (Cost_Install). E.On = Included all heat pump and installation costs under Cost_HP. The Cost_HP and Cost_Install columns can be summed together to gain a comparative "Installed Heat Pump" cost.
4.2 | Equipment Costs - Thermal Store (£) | Cost_TS | Real Number | Cost of the thermal store unit(s) installed | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future.
4.2 | Installation Costs - System (£) | Cost_Install | Real Number | Cost of heat pump system installation - heat pump, thermal store, pipework, etc. | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future. All of the three Delivery Contractors recorded costs differently: OVO = Separated out heat pump costs and installation costs Warmworks = Accounted for all variations within heat pump costs (Cost_HP) and included a flat rate for installation costs (Cost_Install). E.On = Included all heat pump and installation costs under Cost_HP. The Cost_HP and Cost_Install columns can be summed together to gain a comparative "Installed Heat Pump" cost.
4.2 | Costs - additional/new heat emitters | Cost_Emitters | Real Number | Combined cost of all new or replacement heat emitters (radiators), including installation. | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future.
4.2 | Equipment Costs - additional cost to meet cooling requirement | Cost_Cooling | Real Number | Additional cost incurred due to making the system capable of providing home cooling - e.g. pipe insulation, etc | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future.
4.2 | Costs - Loft Insulation (£) | Cost_LI | Real Number | Cost of additional loft insulation - materials and installation | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future.
4.2 | Costs - Wall Insulation (£) | Cost_WI | Real Number | Cost of additional wall insulation - materials and installation | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future.
4.2 | Costs - Windows (£) | Cost_Window | Real Number | Cost of additional windows - materials and installation | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future.
4.2 | Costs - Doors (£) | Cost_Door | Real Number | Cost of additional doors - materials and installation | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future.
4.2 | Costs - Draught proofing (£) | Cost_DP | Real Number | Cost of additional draught proofing - materials and installation | GBP | <number> | Any costs quoted are the costs to the EoH project and therefore may not be fully representative of standard commercial rates. Additionally costs quoted are representative of a point in time and therefore may not be applicable in future.
4.2 | Time taken for installation of the main heat pump system (days) | Install_time_HP | Real Number | The total time taken for the entire HP system installation process - heat pump, thermal store, controls and associated plumbing/electrics | Days | <number> | Recorded to half day accuracy. Note that in some cases, the old heating system may have been operating for most of the installation time period. For the GSHP installations, E.On included the external works within the time however the other Delivery Contractors only included the amount of time taken to install the heat pump (i.e. OVO and Warmworks excluded drilling and civil/ground works). The project took place in the midst of the COVID-19 pandemic and therefore time taken may be skewed.
4.2 | Time taken for installation of additional measures (days) | Install_time_measures | Real Number | Time taken for the installation of other measures within the home - doors, insulation, etc | Days | <number> | Recorded to quarter day accuracy. This is recorded as a separate time to the installation of the heat pump system, even if the work was carried out in parallel. The project took place in the midst of the COVID-19 pandemic and therefore time taken may be skewed.

## Interim Performance Summary
The Interim Heat Pump Performance Data Summary dataset is available from the UK Data Archive and USmart.
https://usmart.io/org/esc/discovery?order=statistic.viewCount&tags=BEIS%20EoH%20Project&limit=20&offset=0
Data Item | Field name | Type | Description | Units | Acceptable Values | Attributes / Notes
Property ID Number | Property_ID | String | A randomly allocated pseudonymised identifier for each home. | None | EOH<number> | One per home. Randomly allocated replacing the original House_ID which was the Delivery Contractors customer reference number. Will be replicated in monitoring datasets.
Was the property included in the 12-month analysis? (Flag) | Included_SPF_analysis | Boolean | Flag indicating whether the property was included in the 12-month analysis. | None | TRUE FALSE | 12-month data analysis includes SPF analysis and hybrid heat pump system analysis.
Reason property was excluded from 12-month analysis | Excluded_SPF_analysis_reason | String | If property was excluded from the 12-month data analysis, reason why. | None | Less than 1yr data available; Less than 1yr usable data; No valid 1yr window due to gaps; SPF outside threshold; Quality score outside threshold; Less than 50% expected data available; BLANK | 12-month data analysis includes SPF analysis and hybrid heat pump system analysis. Order is prioritised so only one reason per property given. Blank indicates property was included in analysis.
Raw dataset first datapoint date and time | Whole_dataset_start | Date and Time | The date and time allocated to the first datapoint within the raw dataset for this property. | None | <YYYY-MM-DDThh:mm:ssZ> (ISO format)
Raw dataset last datapoint date and time | Whole_dataset_end | Date and Time | The date and time allocated to the last datapoint within the raw dataset for this property. | None | <YYYY-MM-DDThh:mm:ssZ> (ISO format)
Duration between first and last datapoint in raw dataset | Whole_dataset_duration_days | Real Number | Time elapsed between the first and last datapoint in the raw dataset. | Days | <number> Maximum 2 decimal places
Cleansed dataset first datapoint date and time | Cleansed_dataset_start | Date and Time | The date and time allocated to the first datapoint within the cleansed dataset for this property. | None | <YYYY-MM-DDThh:mm:ssZ> (ISO format)
Cleansed dataset last datapoint date and time | Cleansed_dataset_end | Date and Time | The date and time allocated to the last datapoint within the cleansed dataset for this property. | None | <YYYY-MM-DDThh:mm:ssZ> (ISO format)
Duration between first and last datapoint in cleansed dataset | Cleansed_dataset_duration_days | Real Number | Time elapsed between the first and last datapoint in the cleansed dataset. | Days | <number> Maximum 2 decimal places
Selected 12-month analysis window start (Date and time) | Selected_window_start | Date and Time | The date and time for the first datapoint in the selected 12-month analysis window. | None | <YYYY-MM-DDThh:mm:ssZ> (ISO format) | Window selected based on data quality scoring using data from the cleansed dataset.
Selected 12-month analysis window end (Date and time) | Selected_window_end | Date and Time | The date and time for the last datapoint in the selected 12-month analysis window. | None | <YYYY-MM-DDThh:mm:ssZ> (ISO format) | Window selected based on data quality scoring using data from the cleansed dataset.
Maximum data quality score within the selected 12-month analysis window. | Selected_window_quality_score_max | Real Number | The maximum data quality score attributed to the selected 12-month analysis window during the data quality checks. | None | <number> between 0-5 Maximum 1 decimal place | Higher score indicates worse data quality. Maximum scores of 4 or greater result in the property being excluded from 12-month analysis. Maximum scores between 3 and 4 resulted in a manual check of the data.
Mean data quality score across the selected 12-month analysis window. | Selected_window_quality_score_mean | Real Number | The mean quality score of all the data over the selected 12-month analysis window. | None | <number> between 0-5 Maximum 3 decimal places | Higher score indicates worse data quality.
SPFH2 from the selected data analysis window. | Selected_window_SPFH2 | Real Number | SPFH2 value calculated for the selected window. | None | <number> Maximum 3 decimal places | This is the SPFH2 value used within the data analysis presented in the Insights and Data Analysis report.
SPFH3 from the selected data analysis window. | Selected_window_SPFH3 | Real Number | SPFH3 value calculated for the selected window. | None | <number> Maximum 3 decimal places | This is the SPFH3 value used within the data analysis presented in the Insights and Data Analysis report.
SPFH4 from the selected data analysis window. | Selected_window_SPFH4 | Real Number | SPFH4 value calculated for the selected window. | None | <number> Maximum 3 decimal places | This is the SPFH4 value used within the data analysis presented in the Insights and Data Analysis report.
Whole heating system energy consumed across 12-month analysis window. | Selected_window_Whole_System_Energy_Consumed | Real Number | Energy measured by the Whole System electricity meter over the selected 12-month analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the window.
Heat pump energy output across 12-month analysis window. | Selected_window_HP_Energy_Output | Real Number | Energy measured by the heat pump heat meter over the selected 12-month analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the window.
Immersion heater energy consumed across 12-month analysis window. | Selected_window_IH_Energy_Consumed | Real Number | Energy measured by the immersion heater electricity meter over the selected 12-month analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the window. Where no immersion heater is present then the datapoint is left blank.
Back-up heater energy consumed across 12-month analysis window. | Selected_window_BUH_Energy_Consumed | Real Number | Energy measured by the back-up heater electricity meter over the selected 12-month analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the window. Where either no back-up heater is present or back-up heater is not sub-metered, this datapoint will be blank.
Circulation pump energy consumed across 12-month analysis window. | Selected_window_CP_Energy_Consumed | Real Number | Energy measured by the circulation pump electricity meter over the selected 12-month analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the window.
Boiler energy output across 12-month analysis window. | Selected_window_Boiler_Energy_Output | Real Number | Energy measured by the boiler heat meter over the selected 12-month analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the window. For non-hybrid systems this datapoint is left blank.
Mean space heating flow temperature across 12-month analysis window. | Selected_window_mean_SH_flow_temp | Real Number | Mean heating flow temperature calculated for the selected 12-month analysis window. | ⷪC | <number> Maximum 2 decimal places | This is calculated for times when the heat pump was outputting heat and this was not recorded as being for domestic hot water heating.
Mean space heating return temperature across 12-month analysis window. | Selected_window_mean_SH_return_temp | Real Number | Mean heating return temperature calculated for the selected 12-month analysis window. | ⷪC | <number> Maximum 2 decimal places | This is calculated for times when the heat pump was outputting heat and this was not recorded as being for domestic hot water heating.
Mean hot water flow temperature across 12-month analysis window. | Selected_window_mean_HW_Flow_Temp | Real Number | Mean reading for Hot_Water_Flow_Temperature during the selected 12-month analysis window. | ⷪC | <number> Maximum 2 decimal places
Did the heat pump operate with a flow temperature above 65C? (Flag) | Selected_window_flow_>65C_flag | Boolean | Flag indicating whether either readings from sensors Heat_Pump_Heating_Flow_Temperature or Heat_Pump_Hot_Water_Flow_Temperature were >65ⷪC during the selected 12-month analysis window. | None | TRUE FALSE | Blank indicates that home was not included in 12-month analysis.
Proportion of time heat pump flow temperature was above 65C. | Selected_window_proportion_flow_>65C | Real Number | Proportion of Heat_Pump_Heating_Flow_Temperature and Heat_Pump_Hot_Water_Flow_Temperature readings >65ⷪC | None | <number> Maximum 4 decimal places | Proportion where a value of 1 equals 100%. Blank indicates that the heat pump did not operate with a flow temperature above 65 degrees celcius. Zero value indicates that the heat pump operated with a flow temperature above 65 degrees celcius less than 0.01% of the time.
Proportion of whole system energy consumed data available in the 12-month analysis window. | SW_proportion_complete_Whole_System_Energy_Consumed | Real Number | The proportion of available data from the whole system energy consumed sensor across the selected 12-month analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of heat pump energy output data available in the 12-month analysis window. | SW_proportion_complete_HP_Energy_Output | Real Number | The proportion of available data from the heat pump energy output sensor across the selected 12-month analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of immersion heater energy consumed data available in the 12-month analysis window. | SW_proportion_complete_IH_Energy_Consumed | Real Number | The proportion of available data from the immersion heater energy consumed sensor across the selected 12-month analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of back-up heater energy consumed data available in the 12-month analysis window. | SW_proportion_complete_BUH_Energy_Consumed | Real Number | The proportion of available data from the back-up heater energy consumed sensor across the selected 12-month analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of circulation pump energy consumed data available in the 12-month analysis window. | SW_proportion_complete_CP_Energy_Consumed | Real Number | The proportion of available data from the circulation pump energy consumed sensor across the selected 12-month analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of boiler energy output data available in the 12-month analysis window. | SW_proportion_complete_Boiler_Energy_Output | Real Number | The proportion of available data from the boiler energy output sensor across the selected 12-month analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Count of all acceptable data analysis windows. | Acceptable_windows_count | Integer | The number of 1 year windows with at least 1 day separation found within the data | None | <number>
Mean SPFH2 across all acceptable data analysis windows. | Acceptable_windows_SPFH2_mean | Real Number | Mean of all calculated SPFH2 values, from all 1 year windows with at least 1 day separation. | None | <number> Maximum 3 decimal places | Calculated by first calculating all possible SPFH2 values (from all possible 12-month windows separated by 1 day) and then taking a mean of these results. Not used within analysis. Calculated to test bias in the data analysis method.
Standard deviation for SPFH2 across all acceptable data analysis windows. | Acceptable_windows_SPFH2_std | Real Number | Standard deviation of all calculated SPFH2 values, from all 1 year windows with at least 1 day separation. | None | <number> Maximum 3 decimal places | Calculated by first calculating all possible SPFH2 values (from all possible 12-month windows separated by 1 day) and then taking a standard deviation of these results. Not used within analysis. Calculated to test bias in the data analysis method.
Median SPFH2 across all acceptable data analysis windows. | Acceptable_windows_SPFH2_median | Real Number | Median of all calculated SPFH2 values, from all 1 year windows with at least 1 day separation. | None | <number> Maximum 3 decimal places | Calculated by first calculating all possible SPFH2 values (from all possible 12-month windows separated by 1 day) and then taking a median of these results. Not used within analysis. Calculated to test bias in the data analysis method.
Mean SPFH3 across all acceptable data analysis windows. | Acceptable_windows_SPFH3_mean | Real Number | Mean of all calculated SPFH3 values, from all 1 year windows with at least 1 day separation. | None | <number> Maximum 3 decimal places | Calculated by first calculating all possible SPFH3 values (from all possible 12-month windows separated by 1 day) and then taking a mean of these results. Not used within analysis. Calculated to test bias in the data analysis method.
Standard deviation for SPFH3 across all acceptable data analysis windows. | Acceptable_windows_SPFH3_std | Real Number | Standard deviation of all calculated SPFH3 values, from all 1 year windows with at least 1 day separation. | None | <number> Maximum 3 decimal places | Calculated by first calculating all possible SPFH3 values (from all possible 12-month windows separated by 1 day) and then taking a standard deviation of these results. Not used within analysis. Calculated to test bias in the data analysis method.
Median SPFH3 across all acceptable data analysis windows. | Acceptable_windows_SPFH3_median | Real Number | Median of all calculated SPFH3 values, from all 1 year windows with at least 1 day separation. | None | <number> Maximum 3 decimal places | Calculated by first calculating all possible SPFH3 values (from all possible 12-month windows separated by 1 day) and then taking a median of these results. Not used within analysis. Calculated to test bias in the data analysis method.
Mean SPFH4 across all acceptable data analysis windows. | Acceptable_windows_SPFH4_mean | Real Number | Mean of all calculated SPFH4 values, from all 1 year windows with at least 1 day separation. | None | <number> Maximum 3 decimal places | Calculated by first calculating all possible SPFH4 values (from all possible 12-month windows separated by 1 day) and then taking a mean of these results. Not used within analysis. Calculated to test bias in the data analysis method.
Standard deviation for SPFH4 across all acceptable data analysis windows. | Acceptable_windows_SPFH4_std | Real Number | Standard deviation of all calculated SPFH4 values, from all 1 year windows with at least 1 day separation. | None | <number> Maximum 3 decimal places | Calculated by first calculating all possible SPFH4 values (from all possible 12-month windows separated by 1 day) and then taking a standard deviation of these results. Not used within analysis. Calculated to test bias in the data analysis method.
Median SPFH4 across all acceptable data analysis windows. | Acceptable_windows_SPFH4_median | Real Number | Median of all calculated SPFH4 values, from all 1 year windows with at least 1 day separation. | None | <number> Maximum 3 decimal places | Calculated by first calculating all possible SPFH4 values (from all possible 12-month windows separated by 1 day) and then taking a median of these results. Not used within analysis. Calculated to test bias in the data analysis method.
Was the property included in the coldest day analysis? (Flag) | Included_coldest_day_analysis | Boolean | Flag indicating whether the property was included in the coldest day analysis. | None | TRUE FALSE
Reason property was excluded from coldest day analysis | Excluded_coldest_day_analysis_reason | String | If property was excluded from the coldest day data analysis, reason why. | None | Not ASHP; Insufficient Data Available; COP Outside of acceptable range; Coldest day not in winter; Heat Pump Energy Output Outside of acceptable range; BLANK
Start of the coldest day analysis window (Date and time) | Coldest_day_start | Date and Time | The first timestamp during the coldest day with any heating load. | None | <YYYY-MM-DDThh:mm:ssZ> (ISO format)
COPH4 calculated across the coldest day analysis window. | Coldest_day_COPH4 | Real Number | COP calculated for the coldest day (using H4 boundary) | None | <number> Maximum 3 decimal places
Mean external temperature across the coldest day analysis window. | Coldest_day_External_Air_Temp_mean | Real Number | Mean External_Air_Temperature during the coldest day | ⷪC | <number> Maximum 2 decimal places
Max external temperature within the coldest day analysis window. | Coldest_day_External_Air_Temp_max | Real Number | Maximum External_Air_Temperature during the coldest day | ⷪC | <number> Maximum 2 decimal places
Min external temperature within the coldest day analysis window. | Coldest_day_External_Air_Temp_min | Real Number | Minimum External_Air_Temperature during the coldest day | ⷪC | <number> Maximum 2 decimal places
Mean internal temperature across the coldest day analysis window. | Coldest_day_Internal_Air_Temp_mean | Real Number | Mean Internal_Air_Temperature during the coldest day | ⷪC | <number> Maximum 2 decimal places
Max internal temperature within the coldest day analysis window. | Coldest_day_Internal_Air_Temp_max | Real Number | Maximum Internal_Air_Temperature during the coldest day | ⷪC | <number> Maximum 2 decimal places
Min internal temperature within the coldest day analysis window. | Coldest_day_Internal_Air_Temp_min | Real Number | Minimum Internal_Air_Temperature during the coldest day | ⷪC | <number> Maximum 2 decimal places
Whole heating system energy consumed across coldest day analysis window. | Coldest_day_Whole_System_Energy_Consumed | Real Number | Energy measured by the Whole System electricity meter over the coldest day analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the coldest day window.
Heat pump energy output across coldest day analysis window. | Coldest_day_HP_Energy_Output | Real Number | Energy measured by the heat pump heat meter over the coldest day analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the coldest day window.
Immersion heater energy consumed across coldest day analysis window. | Coldest_day_IH_Energy_Consumed | Real Number | Energy measured by the immersion heater electricity meter over the coldest day analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the coldest day window. Where no immersion heater is present then the datapoint is left blank.
Back-up heater energy consumed across coldest day analysis window. | Coldest_day_BUH_Energy_Consumed | Real Number | Energy measured by the back-up heater electricity meter over the coldest day analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the coldest day window. Where either no back-up heater is present or back-up heater is not sub-metered, this datapoint will be blank.
Circulation pump energy consumed across coldest day analysis window. | Coldest_day_CP_Energy_Consumed | Real Number | Energy measured by the circulation pump electricity meter over the coldest day analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the coldest day window.
Boiler energy output across coldest day analysis window. | Coldest_day_Boiler_Energy_Output | Real Number | Energy measured by the boiler heat meter over the coldest day analysis window. | kWh | <number> Maximum 2 decimal places | This is the difference between cumulative readings at the start and end of the coldest day window. For non-hybrid systems this datapoint is left blank.
Proportion of whole system energy consumed data available in the coldest day analysis window. | CD_proportion_complete_Whole_System_Energy_Consumed | Real Number | The proportion of available data from the whole system energy consumed sensor across the coldest day analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of heat pump energy output data available in the coldest day analysis window. | CD_proportion_complete_HP_Energy_Output | Real Number | The proportion of available data from the heat pump energy output sensor across the coldest day analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of immersion heater energy consumed data available in the coldest day analysis window. | CD_proportion_complete_IH_Energy_Consumed | Real Number | The proportion of available data from the immersion heater energy consumed sensor across the coldest day analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of back-up heater energy consumed data available in the coldest day analysis window. | CD_proportion_complete_BUH_Energy_Consumed | Real Number | The proportion of available data from the back-up heater energy consumed sensor across the coldest day analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of circulation pump energy consumed data available in the coldest day analysis window. | CD_proportion_complete_CP_Energy_Consumed | Real Number | The proportion of available data from the circulation pump energy consumed sensor across the coldest day analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Proportion of boiler energy output data available in the coldest day analysis window. | CD_proportion_complete_Boiler_Energy_Output | Real Number | The proportion of available data from the boiler energy output sensor across the coldest day analysis window. | None | <number> Maximum 3 decimal places | This calculated using (number of data points)/(expected number of data points). Therefore a value of 1 equals 100% expected data available.
Was the temperature cleaning successful? (Flag) | Temp_cleaning_complete | Boolean | Flag indicating the outcome of temperature data cleaning for this home. | None | TRUE FALSE | Temperature cleaning is unsuccessful if heat pump flow, return and hot water temperature sensors had <50% of their expected readings ( and therefore checking if sensors were swapped [i.e mis-labelled] was not possible ).
Was a partial swap of the hot water flow temperature data and heating flow temperature completed? | Hot_water_flow_temperature_partial_swap | String | Indication of whether the temperature cleaning process resulted in a partial swap between the data in the hot water flow temperature column and that in the space heating flow temperature column. | None | Completed; Attempted; BLANK | Completed = Full swap completed Attempted = Full swap attempted but not completed due to complications. Blank cell indicates no swap was deemed necessary.
Was a full swap of the hot water flow temperature data and heating flow temperature completed? | Hot_water_flow_temperature_full_swap | String | Indication of whether the temperature cleaning process resulted in a full swap between the data in the hot water flow temperature column and that in the space heating flow temperature column. Completed = Full swap completed Attempted = Full swap attempted but not completed due to complications. Blank cell indicates no swap was deemed necessary. | None | Completed; Attempted; BLANK | Completed = Full swap completed Attempted = Full swap attempted but not completed due to complications. Blank cell indicates no swap was deemed necessary.

## Performance - Raw Public
Overview
The raw data is contained within a series of .csv files. Each of these files contains the raw monitored heat pump performance data from one of the properties. The filenames for the .csv files are the unique Property_ID number. As such, each properties data can be referenced back to (and analysed alongside) the other project datasets. The raw dataset contains only 3 columns as below. These indicate what time the data was collected, what type of data is in the row and the data value. This is converted into a more useable format within the cleansed dataset. The raw and cleansed heat pump performance datasets are available on the UK Data Archive.
Field name | Type | Description | Units | Acceptable Values | Attributes / Notes
Timestamp | Date and Time | The exact time that this datapoint was collected. | None | <YYYY-MM-DD Thh:mm:ss> (ISO format) | The exact time when the datapoint was collected.
Sensor_Type | String | The type of data which has been collected. | None | Back-up_Heater_Energy_Consumed; Boiler_Energy_Output; Brine_Flow_Temperature; Brine_Return_Temperature; Circulation_Pump_Energy_Consumed; External_Air_Temperature; Heat_Pump_Energy_Output; Heat_Pump_Heating_Flow_Temperature; Heat_Pump_Return_Temperature; Hot_Water_Flow_Temperature; Immersion_Heater_Energy_Consumed; Internal_Air_Temperature; Whole_System_Energy_Consumed | This field indicates the type of data which has been collected by referencing the sensor which collected the data.
Value | Real Number | The value of the data collected. | See below | <number> | Note. Some values are cumulative and others are instantaneous, as noted below.
Sensor / Data Type Breakdown
|  | Sensor_Type | Units | Data Type | Data Collection Equipment and Description
|  | Back-up_Heater_Energy_Consumed | kWh | Cumulative | Eastron SDM120. Where it forms part of the system, the back-up heater should be located within the internal heat pump unit or be directly plumbed into the primary heating system flow pipework.
|  | Boiler_Energy_Output | kWh | Cumulative | Sontex SuperStatic 440 adjusted for 1Wh energy reporting. Hybrid only. Similar to heat pump energy output but for the gas boiler. Should measure only the gas boiler output.
|  | Brine_Flow_Temperature | 0C | Instantaneous | Sontex SuperCal 531. GSHP only. Sensor located on the flow pipework of the brine loop after it leaves the heat pump system.
|  | Brine_Return_Temperature | 0C | Instantaneous | Sontex SuperCal 531. GSHP only. Sensor located on the return pipework of the brine loop after it leaves the heat pump system.
|  | Circulation_Pump_Energy_Consumed | kWh | Cumulative | Eastron SDM630Modbus. Where systems have multiple circulation pumps the meter should capture the energy used by all of them.
|  | External_Air_Temperature | 0C | Instantaneous | Record sent from local weather station readings.
|  | Heat_Pump_Energy_Output | kWh | Cumulative | Sontex SuperStatic 440 calibrated for DTX glycol where required. Contains temperature sensors and a flow meter and automatically calculates kWh output using these. Located as close as possible to the heat pump on the primary flow and return pipework such that it measures only the heat pump energy output.
|  | Heat_Pump_Heating_Flow_Temperature | 0C | Instantaneous | Sontex SuperStatic 440. Reading is measured by a temperature sensor which forms part of the heat meter only when in heating mode (mode is detected by monitoring the diverter valve).
|  | Heat_Pump_Return_Temperature | 0C | Instantaneous | Sontex SuperStatic 440. Reading is measured by a temperature sensor which forms part of the heat meter.
|  | Hot_Water_Flow_Temperature | 0C | Instantaneous | Sontex SuperStatic 440. Reading is measured by a temperature sensor which forms part of the heat meter only when in hot water mode (mode is detected by monitoring the diverter valve).
|  | Immersion_Heater_Energy_Consumed | kWh | Cumulative | Eastron SDM120. Where it forms part of the system, the immersion heater should be located in the primary thermal storage.
|  | Internal_Air_Temperature | 0C | Instantaneous | DH-SES-302. Sensor installed somewhere within the home. Only one per home, should be centrally located and away from direct sunlight.
|  | Whole_System_Energy_Consumed | kWh | Cumulative | Eastron SDM630Modbus. Located on the primary wiring for the whole heat pump system. Measures all of the electrical energy consumed by the system. Heat Pump Energy Consumed derived by taking this and subtracting all other electricity meter readings.

## Performance - Cleansed Public
Overview
The cleansed data is contained within a series of .csv files. Each of these files contains the cleansed monitored heat pump performance data from one of the properties. The filenames for the .csv files are the unique Property_ID number. As such, each properties data can be referenced back to (and analysed alongside) the other project datasets. Each cleansed dataset contains only columns related to which data was collected for that property (i.e. a non-hybrid system will not have a Boiler_Energy_Output column). The below list is a list of all possible data columns however, no property will contain all of these columns. The raw and cleansed heat pump performance datasets are available on the UK Data Archive.
Field name | Type | Description | Units | Acceptable Values | Attributes / Notes
Timestamp | Date and Time | The exact time that this datapoint was collected. | None | <YYYY-MM-DD Thh:mm:ss> (ISO format) | The exact time when the datapoint was collected.
Back-up_Heater_Energy_Consumed | Real Number | Cumulative back-up heater energy consumed data. | kWh | <number> | Data collected by Eastron SDM120. Where it forms part of the system, the back-up heater should be located within the internal heat pump unit or be directly plumbed into the primary heating system flow pipework.
Boiler_Energy_Output | Real Number | Cumulative boiler energy output data. | kWh | <number> | Data collected by Sontex SuperStatic 440 adjusted for 1Wh energy reporting. Hybrid only. Similar to heat pump energy output but for the gas boiler. Should measure only the gas boiler output.
Brine_Flow_Temperature | Real Number | Non-cumulative brine flow temperature data. | 0C | <number> | Data collected by Sontex SuperCal 531. GSHP only. Sensor located on the flow pipework of the brine loop after it leaves the heat pump system.
Brine_Return_Temperature | Real Number | Non-cumulative brine return temperature data. | 0C | <number> | Data collected by Sontex SuperCal 531. GSHP only. Sensor located on the return pipework of the brine loop after it leaves the heat pump system.
Circulation_Pump_Energy_Consumed | Real Number | Cumulative circulation pump energy consumed data. | kWh | <number> | Data collected by Eastron SDM630Modbus. Where systems have multiple circulation pumps the meter should capture the energy used by all of them.
External_Air_Temperature | Real Number | Non-cumulative external air temperature data. | 0C | <number> | Record sent from local weather station readings.
Heat_Pump_Energy_Output | Real Number | Cumulative heat pump energy output data. | kWh | <number> | Data collected by Sontex SuperStatic 440 calibrated for DTX glycol where required. Contains temperature sensors and a flow meter and automatically calculates kWh output using these. Located as close as possible to the heat pump on the primary flow and return pipework such that it measures only the heat pump energy output.
Heat_Pump_Heating_Flow_Temperature | Real Number | Non-cumulative heat pump heating flow temperature data. | 0C | <number> | Data collected by Sontex SuperStatic 440. Reading is measured by a temperature sensor which forms part of the heat meter only when in heating mode (mode is detected by monitoring the diverter valve).
Heat_Pump_Return_Temperature | Real Number | Non-cumulative heat pump return temperature data. | 0C | <number> | Data collected by Sontex SuperStatic 440. Reading is measured by a temperature sensor which forms part of the heat meter.
Hot_Water_Flow_Temperature | Real Number | Non-cumulative hot water flow temperature data. | 0C | <number> | Data collected by Sontex SuperStatic 440. Reading is measured by a temperature sensor which forms part of the heat meter only when in hot water mode (mode is detected by monitoring the diverter valve).
Immersion_Heater_Energy_Consumed | Real Number | Cumulative immersion heater energy consumed data. | kWh | <number> | Data collected by Eastron SDM120. Where it forms part of the system, the immersion heater should be located in the primary thermal storage.
Internal_Air_Temperature | Real Number | Non-cumulative internal air temperature data. | 0C | <number> | Data collected using DH-SES-302. Sensor installed somewhere within the home. Only one per home, should be centrally located and away from direct sunlight.
Whole_System_Energy_Consumed | Real Number | Cumulative whole system energy consumed data. | kWh | <number> | Data collected by Eastron SDM630Modbus. Located on the primary wiring for the whole heat pump system. Measures all of the electrical energy consumed by the system. Heat Pump Energy Consumed derived by taking this and subtracting all other electricity meter readings.

## Reason codes
(2) Recruitment - Interest in Project |  | (4.1) Design - Install not recommended |  | 4.1 (Design) - Participant decision not to proceed
Code | Definition | Code | Definition | Code | Definition
Sustainability | Participant is interested or keen to take action to reduce their environmental impact and/or to move to a greener/renewable heating system | Participant_Suitability | Proposed participant is not believed to be suitable for the project - for example they may be in or at risk of fuel poverty, may have an underlying health condition of concern, etc | Social_TechConf | General concerns about the technology, perhaps due to lack of familiarity, confidence in long term performance, etc
Future | Participant is keen to "future proof" their house / heating system investment by adopting a low carbon technology | Economic_RunningCosts | The projected running costs of the system are believed to be too high for the proposed participant - for example may cause them financial hardship in future. | Social_Perception | Concern about the potential impact on perception of the home - for example could it make it more difficult to sell, etc
Upgrade | Participant is looking for a way to upgrade their heating system and views a Heat pump as a way of doing this. | Economic_InstallCosts | Expected installation cost of the heat pump system (excluding additional measures) is too high for the project budget | Economic_RunningCosts | Not happy with the projected running costs of the system - i.e. too high
Building | Participant is undertaking building / refurbinshment works to their property and would like to take advantage of this | Economic_MeasuresCosts | The cost of additional measures for the home (e.g. insulation, windows, etc) required to make the heat pump work well, are prohibitive for the scope of this project | Economic_MaintenanceCosts | Concerns about cost of system upkeep and maintenance
Financial | Participant is attracted to the fact that the system will be provided free of charge. | Practical_AdditionalMeasures | The scope/scale of additional measures required to make the home suitable for a heat pump is deemed beyond the scope of this project | Practical_DisruptionTime | Partipant is unwilling or unable to accept the time required to install the system
Technology | Participant is intrigued by the technology and/or keen to adopt new technology into their home. | Practical_SpaceExternal | There is no practical external space to site heat pump system components - e.g. no space of sufficient size, in the right area to route into the home, secure, etc | Practical_DisruptionWorks | Participant is unhappy with the proposed level of disruption from the work required to fit the system - e.g. damage to décor, changes to rooms, etc
Research | Participant is keen to support / take part in this research project | Practical_SpaceInternal | There is no practical internal space to site some of the heat pump system components, e.g. no sensible location for a thermal store | Practical_AdditionalMeasures | Concerns or objections to additional measures recommended for the home such as wall insulation, etc
Planned | Participant is already planning to change to a heat pump so this is an opportunity to do so. | Practical_Routing | Required routing of system components (e.g. pipework) is impractical - for example pipe runs too long, require significant disruption or modifications to the home, etc | Practical_SpaceExternal | Objections regarding the space occupied by the Heat Pump system outside the home. Could be physical size or proposed location
Replacement | Existing heating system is in need of replacement anyway so this is an opportunty to achieve that aim | Practical_DisruptionWorks | Level of disruption to the home required is judged to be excessive for the DC to undertake or excessive for the Participant to live with | Practical_SpaceInternal | Objections to the space required within the home to fit the system - e.g. for heat pump units, water tank, etc
Other | Any other reason | Practical_Noise | It is not possible to site a heat pump in a location that complies with Noise regulations. | Practical_Aesthetics | Objections to the aesthetics of the heat pump units or any other aspect of the system installation.
|  | Practical_Reinforcement | DNO has stated that the local network would require reinforcement to permit this installation and this cannot be accomodated within the project | Practical_Noise | Concerns about potential system Noise
|  | Practical_Fabric | There are issues with the building fabric that make a heat pump installation not advisable or risky - e.g. presence of asbestos, poor standard of maintanance. | Technical_Comfort | Concerns about the ability of the Heat Pump system to meet comfort requiremnts
|  | Programme_Cancelled | Progression to installation was cancelled due to there being insufficient time to start and/or complete works before the end of the project installation phase (end Sept 2021) | Supply_Maintenance | Concerns about the long term ability to have the system maintained and supported by the supply chain
|  | Programme_TargetMet | Project targets for a particular home archetype / age / Social group have already been met so home/participant is not required. | Other | Any other reason
|  | Technical_Comfort | Designer does not believe that comfort requirements can be met for the home in question - e.g. warm-up times too long, some problematic rooms in the home, etc
|  | Technical_Size | The size / power of the heat pump system required for the home is beyond the scope of the project or no suitable system is available.
|  | Other | Any other reason